Development of Emergency Operating Guidelines for a Research Reactor

Hyeonil Kim1, S.K. Park1

- Korea Atomic Energy Research Institute, 989-111 Daedeok-daerho, Yuseong, Daejeon, 305-353, Korea

Corresponding author: hyeonilkim@kaeri.re.kr

Abstract. After the Three Mile Island (TMI) accident, much more attention has been paid for establishing emergency operating procedures for nuclear power plants. In addition, many more issues regarding both the reliability and control of a nuclear reactor after post-accident have become a concern since the accident at the Fukushima Daiichi nuclear power plant. In Korea, it is being recommended to follow the practices and legal requirements based on nuclear power plants for further enhancing the safety of a research reactor, although this may be too much.

With the Korean legal requirements [1][2][3][4] for research reactors, many practices were reviewed from the already established guidelines or procedures for nuclear power plants over the world such as the US CE, US Westinghouse, Germany, and Korea. Finally, a set of EOG were developed for two categories: 1) an event-based structure, where from the standard post trip action, the diagnostic action, the specific event-based guidelines such as a reactor trip, loss of normal power, and loss of coolant accident are constructed, and 2) a symptom-based guideline to cover any kind of accident including beyond design basis accidents.

The design for a research reactor was extensively and comprehensively investigated based on the safety functions implemented into the research reactor: 1) reactivity control, 2) maintenance of auxiliary systems, 3) coolant inventory control, 4) core heat removal, and 5) confinement isolation in order of importance and urgency. The five safety functions are the fundamentals in order to operate and manage the reactor, and finally to keep the reactor in a safe shutdown condition during and after an emergency.

The guidelines will be incorporated into EOP that may reflect the real circumstances in a research reactor, and will be validated through a proper review and exercise with the support of a simulator of the reactor.

1. Introduction

Following the Three Mile Island Unit 2 (TMI-2) accident, the United States Nuclear Regulatory Commission (NRC) established the sets of requirements addressing their objective to improve the quality of operational information for dealing with emergency events in nuclear power plants. [5~8]

The Emergency Operating Guidelines (EOG) should be presented to provide technical information to prepare reactor-specific Emergency Operating Procedures (EOP) which cover operation during emergency events.

Applicants for operating license and licensees of reactors under construction are required to:

- Perform analyses of transients and accidents including multiple failures

- Prepare emergency operating guidelines

- Upgrade emergency procedures, including procedures for operating with natural circulation conditions

- Conduct operator retraining

The Procedure Generation Package (PGP) should be submitted to the regulatory body in Korea for the reactor licensing at the same time with Final Safety Analysis Report (FSAR), where PGP includes:

- Reactor-Specific Technical Guidelines (RSTGs),

- EOP Writer's Guide,

- EOP Verification Procedure

- EOP Validation Procedure

- EOP Training Program

- EOP Implementation Program

The information should comply with those requirements associated with the development of EOG according to the Korean atomic law [1][2][3][4]. All assumptions made in the EOP, which relate to safety analysis, must be verified to be true and appropriate for each user by each user.

In research reactors, a set of EOP are required as one of operating procedures that shall be developed for all safety related operations that may be conducted over the entire lifetime of the facility by a standard, Safety of Research Reactors (IAEA NS-R-4) [9]: 7.51 (g) the reactor operator’s response to anticipated operational occurrences and DBAs and, to the extent feasible, to BDBAs. In addition, one more example for categorization and list of operating procedures is presented in a standard, Operational Limits and Conditions and Operating Procedures for Research Reactors (IAEA NS-G-4.4) [10]: 4.21 (g) Procedures for operator responses to anticipated operational occurrences, (h) Emergency procedures.

In Korea, the regulation on codes and standards for nuclear facilities [1][2][3][4] such as research reactors (the regulations for research reactors was developed based on those for Pressurized Light Water Power Reactors) insists the nuclear facilities operating organization prepare EOP. Hence a set of EOG is required for helping to develop the EOP.

In this paper, it is described about a development of a set of EOG for a research reactor rated to 5MW.

2. EOG System

This chapter contains the methodology, which was used to develop and validate the EOG, and information on guideline implementation.

The EOG were developed by incorporating reactor-specific information, and operating experiences of the HANARO, reference practices of Nuclear Power Plants (NPPs).

The essential elements of the EOG are preserved in the development of EOG. These elements include EOG system structure, major event strategy, safety function concept, safety function status check, and success paths.

2.1 Overview of EOG System

A goal of the EOG is to provide the best available technical information to be used for developing reactor-specific EOP. Each reactor has an extensive network of procedures. EOP must be coordinated with the existing procedures. The content and scope of the EOP developed from EOG should be designed to interface with, but neither overlap nor duplicate, reactor procedures. The EOG are designed to be used independently and cross referencing is minimized. Cross referencing is appropriate only when the other guideline entry conditions are achieved during the course of operation. The EOG do not cover information related to overall operation of the reactor site during emergency conditions because that subject is covered by the Site Emergency Plan (SEP).

An understanding of what constitutes an emergency is a prerequisite to deciding what information is to be collected and in which format that information is to be arranged. For the purpose of the EOG, an emergency event is distinguished from other off-normal reactor operations by virtue of its severity; it is sufficiently severe that a reactor trip is either activated automatically or required to be manually initiated to mitigate the event. FIG. 1 depicts the distinction between emergency operating procedures based on these guidelines and other off-normal procedures.

Emergency events can be divided into two classes: 1) the operators can ascertain the general type of the event by recognizing its correlated symptom set from control board indications and their knowledge of the reactor and recent operating history. For these events where an accurate diagnosis can be made, it is highly desirable to provide mitigating guidance which is selected and sequenced to strategically address that symptom set. Since these types of events have been well analyzed and understood (e.g., Loss of Coolant Accident (LOCA), Loss of normal Electric Power (LOEP), and etc.), it is possible to write the event-based recovery emergency operating procedure guidelines to optimize the recovery (i.e., minimize release of radiation, minimize system leakage, reduce risk of core damage, etc.). For ease of use, these events have been grouped; 2) the operators are unable to identify a unique symptom set for the disturbance. This may be due to errors in symptom assessment by the operators; multiple, simultaneous failures in the reactor (e.g., combined LOCA and LOEP, and etc.); the occurrence of a heretofore unanalyzed event (e.g., loss of flow capability, and etc.); or instrumentation failures which distort the symptom picture.

EOG must provide guidance for both classes of emergencies. Thus, when a reactor trip occurs or should occur, the operators can refer to guidance which will provide a safe response whether or not a symptom set is identified: EOG written to treat specific symptoms are called event-based recovery guidelines (ERG); the EOG which provides guidance for undiagnosed events for which a reactor trip is required is called the Symptom-based Recovery Guidelines (SRGs).

- FIG. 1. Overall view of operational procedure

FIG. 2 illustrates an example of the system of EOG. The EOG can be entered in one of two ways, depending upon the reactor status at the time of event initiation. The Standard Post Trip Actions (SPTA), which are performed following all reactor trips (automatically or manually initiated), is the entry point for the EOG if the event is initiated from Operation Mode Power. Its purpose is to evaluate the status of each safety function and to provide immediate actions which can be quickly and easily performed to improve the status of safety functions in jeopardy. Following the SPTA, the Diagnostic Actions (DA) are performed to determine the symptom set corresponding to the type of event in progress. Depending on the operator's ability to diagnose, they will then select either an ERG or the SRG.

The Symptom-based Recovery Guideline (SRG) may also be entered if the event is initiated from Operation Mode Shutdown. In this case, the Standard Post Trip Actions are not performed (since they may not be applicable). Therefore, the operator enters directly to the Diagnostic Actions prior to entering the SRG if an event is initiated from operation mode Power. Once in the guideline, the operator uses the Safety Function Status Check to confirm that the guideline is providing the appropriate instructions for maintaining safety functions and mitigating the event.

The design of the EOG recognizes that it will become eventually necessary for the operator to specify what resources are available to continue to satisfy safety functions in the course of an emergency. This is necessary because the operators must know what systems and equipment are available for use either in continued operation or for taking the reactor to safe shutdown conditions. The system of EOG also recognizes the possibility of a misdiagnosis by the operators and makes provisions for detecting and recovering from such misdiagnoses. If the operators have selected the SRG because they cannot diagnose the event, the SRG provides action steps to bring the reactor to a safe, stable condition. Once the SRG has been implemented, the operator will continue within the SRG until the exit conditions have been met. This is accomplished by satisfying the Safety Function Status Check (SFSC) acceptance criteria for each success path in use and meeting the entry conditions of an approved procedure. This approved procedure may be an applicable ERG. Naturally, the operators would start at the beginning of the selected ERG to ensure that all the relevant actions have been or are being taken.

Each ERG contains a section which requires the operator to confirm the diagnosis and continually review the status of safety functions by use of the SFSC. If the diagnosis is not confirmed or if the safety function acceptance criteria are not met, the operators then evaluate the need to implement another ERG or the SRG. Thus, if the symptoms are not responding to treatment as anticipated or if the core is not being adequately cooled, the ERG may be terminated and the SRG implemented.

- FIG. 2 An Example of an EOG system

Natural phenomena and other disasters are implicitly addressed in this system since all of the possible consequences of such phenomena which affect the reactor safety are addressed explicitly. Even if such phenomena result in multiple, major consequences, the SRG will provide systematic guidance for managing such a casualty. Therefore, since it is not possible to predict in advance what the consequences to the reactor safety would be for an aircraft crash, and since all possible consequences are covered by the EOG, these phenomena need not be explicitly addressed. Reactor-specific procedures exist for managing non-Safety systems and equipment in the event of certain natural phenomena or man-made disasters.

This EOG will be designed as the basis for emergency operating procedures which provide guidance for operating the reactor to mitigate emergency events. Guidance is provided for operating equipment which is closely associated with the reactor safety. This is in recognition of the existence of non-nuclear safety equipment and systems at each reactor (i.e., balance of reactor) which are important to overall reactor control.

The guidelines are written in a two-column format and do not go into greater detail than system level information. This preserves their generic nature. EOP preparer can write EOP in a format which is most useful to them. Furthermore, guidance for the management of degraded core conditions is not included in these guidelines.

2.2 Safety Functions

2.2.1 The Concept of Safety Functions

The concept of safety functions introduces a systematic approach to reactor operations based on a hierarchy of protective actions. The protective actions are directed at mitigating the consequences of an event and, once fulfilled, ensure proper control of the event in progress. A safety function is defined as a condition or action that prevents core damage or minimizes radiation release to the public. A complete set of safety functions needs to be fulfilled to ensure proper operator control of the event and public safety.

The actions which ensure fulfillment of a safety function may result from automatic or manual actuation of systems, from passive system performance, from natural feedback inherent in the reactor design, or when the operator follows guidance established in an event-based recovery guideline. The operator does not have to know what event has occurred but does have to know what success paths are being utilized and what acceptance criteria must be satisfied.

All safety functions are directed at mitigating an event and containing and/or controlling radioactivity releases. These safety functions can be grouped into four major classes as follows:

- Anti-core melt safety functions

- Confinement isolation safety functions

- Indirect radioactive release safety function

- Maintenance of vital auxiliaries needed to support the other safety functions

The anti-core melt safety function class contains three safety functions:

- Reactivity Control (RC)

- Pool Water Inventory Control (IC)

- Core Heat Removal (CHR)

The purpose of the first anti-core melt safety function, reactivity control, is to shut down the reactor and to keep it shut down condition, thereby reducing the amount of heat generated in the core.

The purpose of pool water inventory control (IC) is to keep the core covered with an effective coolant medium.

The purpose of the third anti-core melt safety function, core heat removal (CHR), is to remove the decay heat generated in the core and transfer it to a location where it can be removed from the PCS.

The confinement isolation safety function class contains single safety function: confinement isolation. The primary objective of this safety function is to prevent major radioactive release from the confinement by maintaining the integrity of the confinement structure.

The third safety function class has one safety function associated with it: indirect radioactive release. The purpose of indirect radioactive release control is to prevent radioactive releases to the environment (gaseous, solid, and liquid, including radioactive coolant) from sources outside confinement. These sources include the radioactive waste handling and storage facilities. The systems used to control releases from these sources include the radiation monitoring system, and the waste management and processing systems. In mitigating the types of emergencies for which this EOG will provide guidance, the indirect radioactive release safety function does not come into play. Consequently, operator actions necessary for control of the indirect radioactive release safety function are not included in this EOG.

The fourth safety function class also includes only one safety function: maintenance of vital auxiliaries. The systems used to accomplish the four other safety functions addressed in THIS EOG are not actually supported by the maintenance of vital auxiliaries. However, in general, support systems provide service such as instrument air needed for opening and closing valves, electric power for valve operation, pump motor operation, and operating instruments and an ultimate heat sink to which PCS and core heat can be transferred. Of greatest impact to the operator actions associated with THIS EOG is AC and DC power. If class-1E AC and DC power are maintained, it would be much more helpful to continue to satisfy the acceptance criteria of the other safety functions and to assure whether the required safety functions are maintained or not.

2.2.2 Safety Function Hierarchy

The safety function concept incorporates a principle of safety function hierarchy. Some safety functions have precedence over others concerning their sequence of implementation during an event. The hierarchy of safety functions is summarized as standardized in this EOG guidance:

- Reactivity Control

- Maintenance of Vital Auxiliaries (AC and DC Power)

- Reactor Pool Water Inventory Control

- Core Heat Removal

- Confinement Isolation

Reactivity control is the most important safety function since it responds most quickly to changes in reactor conditions. Similarly, Reactor Pool Water Inventory Control (IC) must be satisfied before core heat removal can be effected (i.e., there must be a medium to remove heat). This hierarchy concept is important in the design of systems used to fulfill each function and has also been employed in developing the EOG. All of the EOG identify each of the 5 safety functions (in the hierarchy presented previously) and the acceptance criteria which reflect accomplishment of each of the safety functions. The safety functions are provided as a complete set so that the operator can monitor and control the reactor to protect the health and safety of the public.

Application of the concept of safety functions in a restructured format is acceptable as long as: (1) the representation contains actions and acceptance criteria necessary to control and fulfill the five individual safety functions; (2) it is consistent with the safety function hierarchy of this EOG; and (3) the ultimate goal of protecting the health and safety of the public is preserved.

- FIG. 3 Safety Functions Classification

Each level, consisting of a rearrangement or combination of safety functions can achieve the same goal as the set which contains each safety function individually. This safety function subset or rearrangement may be enhanced by use of a particular control room operator aid, etc.

Because safety functions are a complete set of actions or conditions which will provide for the safety of the public, they form the foundation of all EOG. In the ERG, specific events such as LOCA, LOEP are addressed. Because each event affects diverse parts of the reactor, proper mitigation of different events will emphasize different safety functions. For example, in a major LOCA, Reactor Pool Water Inventory Control is the single safety function of immediate concern. Therefore, the operator actions are sequenced to achieve control of this safety function first by using equipment designed for that purpose. Nonetheless, since all safety functions must be fulfilled to provide for the safety of the public, each ERG addresses all of the safety functions.

In preparing EOG, the five safety functions are used to audit the guideline to ensure that sufficient action steps exist to cover all safety functions. Each ERG includes an SFSC which is used by the operator to continually determine whether the safety functions are being adequately fulfilled.

The SRG is used by the operator when a diagnosis is not possible, when the ERG being utilized is not adequate (as judged by the SFSC in each ERG), or when the guideline in use is inappropriate. The SRG structure includes an expanded version of the SFSC which is used by the operator to continually check the status of each safety function. For those safety functions which are found to be in jeopardy, possible success paths are provided along with operator actions for implementing each success path and acceptance criteria by which successful safety function restoration is judged. For this guideline the safety functions form the main structure of the guideline.

2.2.3 Success Paths

Nuclear facilities are designed such that each safety function has multiple means of fulfillment. In other words, for each safety function there may exist more than one system or means of fulfillment called success paths. For example, Reactivity control can be achieved by inserting control rod absorbers or second shutdown rods in the reactor. It is important that the operator be aware of the various success paths associated with each safety function.

3. Principles of Event-based Recovery Guidelines

3.1 Event-based Recovery Guideline Structure

ERG are those guidelines written to address sets of specific symptom. In order to minimize the number of guidelines, and thereby avoid operator confusion, those events which are difficult to distinguish from each other in the short term or which have similar effects on the core over time are grouped into classes of events. The classes of events considered are:

- Reactor Trip (RT)

- Loss Of normal Electric Power (LOEP)/ Loss of Forced Circulation

- Loss of Coolant Accident (LOCA)

Differences between the set of Event-Based Recovery Guidelines (ERG) and the reactor-specific set of Event-Based Recovery Procedures (ERP) are permitted, as long as all of the classes of events covered in the ERG are covered in the ERP (e.g., Loss of normal Electric Power events could be covered in a Loss of Forced Circulation procedure; or the LOEP and Station Blackout ERG could be combined in an Electrical Emergency procedure).

Each ERG consists of the following sections:

- Purpose

- Entry Conditions

- Exit Conditions

- Operator Action Steps

- Safety Function Status Check

- Supplementary Information

- Placekeeper

- Bases

3.2 Use of the Event-based Recovery Guidelines

ERG are used to treat specific symptom sets which are identifiable or diagnosable by the operators following a reactor trip. Each ERG is designed to accommodate minor concurrent failures which do not present major complications. The SPTA and/or DA are performed before an ERG is implemented if the event is initiated from Operation Mode Power. If a specific symptom set can be identified, the operators will then implement the appropriate ERG. The goal of the recovery actions is to place the reactor in a safe and stable condition.

The emphasis in the ERG is on treatment of a set of symptoms according to an optimal strategy, as contrasted to treatment of a specific event. One of the first recovery actions will be to assess the safety functions against specific acceptance criteria using the SFSC. This serves a dual purpose. First, it is a check to verify that all safety functions are being satisfied. Second, it provides a means of verifying that the initial diagnosis was correct. This essential feature provides a correction process. If the guideline in use is adequately treating the symptoms, then the treatment is continued. If the treatment is inadequate, either because new information (symptoms) appears that is not covered in the guideline, or because the observed symptoms are not properly responding, each ERG has a step which requires the operators to exit the ERG and to implement the SRG. The checking process using the SFSC continues as long as the guideline is in use. This is the way the EOG system manages multiple, significant failures, or misdiagnosed or un-diagnosable symptom sets. The EOG is designed to provide guidance for managing any event which results in or requires a reactor trip.

Operator actions are selected and sequenced to address all safety functions in their order of importance to treat that symptom picture. Contingency actions are included, where appropriate, for use when primary success paths have not been successful.

4. Principles of Symptom-based Recovery Guideline

4.1 Symptom-based Recovery Guideline Structure

The SRG is the EOG implemented following a reactor trip in which the event cannot be diagnosed by the operators. It may also be implemented for cases where the operators have initially selected an ERG but subsequently discovered that they had misdiagnosed the event or that the ERG was not adequately maintaining safety functions.

The SRG consists of the following sections:

- Purpose

- Entry Conditions

- Exit Conditions

- SRG Entry Procedure

- Resource Assessment Trees

- Safety Function Status Check

- Placekeeper

- Reactivity Control

- Maintenance of Vital Auxiliaries

- Reactor Pool Water Inventory Control

- Core Heat Removal

- Confinement Isolation

- Long Term Actions

In addition, each guideline contains supplementary information and bases which should be considered when utilizing the EOG to implement reactor-specific EOP.

.

Resource Assessment Trees (RAT)

RAT are pictorial representations of the systems/components available to fulfill each safety function. The trees are intended to assist the operator in evaluating reactor resources available to fulfill jeopardized safety functions. A pictorial representation was chosen for the EOG resource trees for simplicity and clarity. It relies minimally on reading and verbal comprehension and serves as a quick method to jog the operator's memory regarding the systems and components used to fulfill each safety function. The comprehensive knowledge of these systems and components and their proper operation are already available to the operator from training and experience.

Each limb of an RAT starts at the top with the name of the safety function, then (working down) the name of the success path (mode), then the reactor conditions and equipment used in that path (conditions, source, motive, power), and then the acceptance criteria for that success path.

In constructing these resource trees, a number of principles were observed:

- Each success path identified on a resource tree had to be reactor-specific and be capable of independently satisfying that safety function.

- The RAT are structured to show the intended priority (left to right) of implementation of success paths.

- Two rules were used to order the components/conditions from top to bottom in each success path. The first rule is to arrange components according to the normal flow path in the reactor since this is most familiar and logical. The second rule was to attempt to place the most restrictive component, or Reactor conditions or limits, toward the top of the limb. In this way, if the PCS or equipment did not meet this condition, it would spare the operator from reviewing the rest of the limb.

- The limbs are not intended to be detailed representations of reactor systems. They are intended only to serve as an aid to the operator in determining the availability of resources. The limits shown inside each component are intended to provide only the most essential, minimum requirements for success path availability. All limits can be read directly (without interpretation) from control board indications in the control room.

- The minimum amount of information which would assure path availability was included for each limb. That is, if the minimum requirements expressed by the limits in the limb were met, then there is a high probability that the success path will be available. In practice, by the time the operator begins to implement the SRG, they are largely aware of which systems and components are available.

- The acceptance criteria that appear at the bottom of each limb are the same acceptance criteria which appear on the SRG SFSC. Therefore, if the acceptance criteria for the highest numbered limb are met, then the corresponding safety function is fulfilled.

- When this success path information is implemented in reactor-specific EOP, utilities will have the flexibility of changing this pictorial format to some other format. What is necessary is that each utility provide equivalent information in some usable format.

4.2 Use of the Symptom-based Recovery Guideline

The following gives a brief description of how to use the Symptom-based Recovery Guideline:

The SPTA and DA are performed prior to entry into the SRG for an event initiated from Operation Mode Power. The SRG may also be entered in any of the following ways:

- Directly after completion of the SPTA and DA, if a diagnosis is not possible.

- From an ERG, if an ERG had been initially selected by the operator but was subsequently found to be inadequate in dealing with the event. The SFSC in each ERG is the primary means used to judge this adequacy. If the safety function acceptance criteria are not satisfied at any time, then the operator is directed to evaluate implementing the SRG.

- After completion of the DA, if all of the specified entry conditions to Operation Mode Shutdown are met.

The entry point for the SRG is the SRG Entry Procedure. Once a success path has been selected, the operator reviews the status of all safety functions by checking control board indication against the acceptance criteria for the success paths in use. The purpose of this review is to identify those safety functions that are jeopardized, challenged or satisfied. The operator focuses on the jeopardized safety functions first. After completing the appropriate instructions for the safety functions already identified jeopardized, the operator follows the instructions corresponding to those safety functions determined to be being challenged, and then continues to verify that the satisfied safety functions remain satisfied.

If more than one success path are in use for a given safety function, the operator uses the acceptance criteria for the highest numbered success path. For example, if reactor pool water inventory control is the safety function in question and success paths IC-1 and IC-2 are both currently in use, the acceptance criteria for success path IC-2 must be satisfied. This would continue to be true until normal inventory control becomes the sole IC success path in use. Note that the acceptance criteria for the first success path for each safety function generally correspond to the symptoms of a simple reactor trip.

As mentions above, the operator begins with the first safety function which is in jeopardy, and reviews the resource assessment tree to ascertain the availability of resources. Working from left to right on the trees the operator reviews each success path to determine its availability and whether it has been already operating or not. If it is operating, the operator checks the acceptance criteria to see if the safety function acceptance criteria are now being satisfied. If the safety function acceptance criteria are satisfied, the operator goes on to the next safety function in jeopardy. If the success path is required to be operating, and is not operating but is available (as indicated by meeting the component or condition limits noted on each success path), the operator implements the recovery guideline referenced for that path. If the acceptance criteria associated with that success path are now satisfied, the operator goes on to the next safety function in jeopardy. If the acceptance criteria are still not satisfied, the operator goes to the next success path to the right on the tree and continues implementing success paths until the safety function is satisfied. It is possible, and desirable in many cases, to use more than one success path at a time. Even if more than one success path are in use, the acceptance criteria by which the fulfillment of the safety function is judged are those for the highest number success path in use.

If all of the success paths on the RAT have been implemented and none of their respective acceptance criteria are met, then each resource tree has a caution which requires the operator to refer to the "Continuing Actions" section. The operator is required to continue to work on this safety function and to peruse other jeopardized or challenged safety functions simultaneously.

Once all safety functions have been satisfied and appropriate operator actions for all success paths in use have been performed, the operator refers simultaneously to the Long Term Actions to attempt to evaluate reactor status, determine a diagnosis and determine an extended course of action. Concurrent with taking steps to restore jeopardized safety functions, the control room team is using the SRG SFSC to continually review the status of safety functions. As the event progresses and/or as new success paths are available, the operator may have to shift to the new acceptance criteria which correspond to these success paths. This periodic review may reveal that a safety function is in jeopardy and requires further operator action.

5 Summaries

In Korea, a set of Emergency Operating Guidelines (EOG), recommended to follow the practices and legal requirements based on nuclear power plants for further enhancing the safety of a research reactor although it may be too much, have been developed for a research reactor rated to 5MW for two categories: 1) an event-based structure, where from the standard post trip action, the diagnostic action, the specific event-based guidelines such as a reactor trip, loss of normal electric power, and loss of coolant accident are constructed, and 2) a symptom-based guideline to cover any kind of accident including beyond design basis accidents.

The guidelines will be incorporated into EOP that may reflect the real circumstances in a research reactor, and will be validated through a proper review and exercise with the support of a simulator of the reactor.

6. References

- Nuclear Safety Act, 2011.

- Regulation of NSSC, No. 2, Enforcement Regulation of Nuclear Safety Act, 2011.

- Regulation of NSSC, No. 3, Regulation on Technical Criteria for Nuclear Reactor Facilities, 2011.

- Notice of NSSC No. 2012-27, Regulation on Technical Specifications of Construction and Operation Capabilities for Nuclear Reactor Facilities, 2012.

- NUREG-0578, TMI-2 Lessons Learned Task Force Status Report and Short-Term Recommendations, U.S. NRC, July 1979.

- NUREG-0585, TMI-2 Lessons Learned Task Force Final Report.

- NUREG-0660, Action Plan Developed as a Result of the TMI-2 Accident.

- NUREG-0899, Guidelines for the Preparation of Emergency Operating Procedures, 1982.

- Safety Requirements, NS-R-4, Safety of Research Reactors, 2005.

- Safety Guide, NS-G-4.4, Operational Limits and Conditions and Operating Procedures for Research Reactors, 2008.

- Safety Report Series No. 48, Development and Review of Reactor Specific Emergency Operating Procedures, 2006.1515